Bulk Ultrasonic Water Meter (DN50-400)
MODBUS Communication Protocol

V1.23

- The ultrasonic water meter adopts the MODBUS-RTU communication protocol. The MODBUS protocol specifies in detail the checksum and data sequence, which are essential components for specific data exchange. The MODBUS protocol uses a master-slave responder connection (half-duplex) over a single communication line, meaning signals are transmitted in opposite directions on the same communication line. First, the signal from the host computer is sent to a unique terminal device (slave), and then the response signal from the terminal device is transmitted back to the host in the opposite direction.

- The MODBUS protocol only allows communication between the host (computer, PLC, etc.) and the terminal devices, and does not permit direct data exchange between independent terminal devices. This ensures that terminal devices do not occupy the communication line during initialization and only respond to query signals addressed to them.

- The MODBUS-RTU format does not include start or end characters but requires the addition of a waiting time. The waiting time must be at least 3.5 characters.

- Precautions:

- 1. The meter requires DC for communication and power supply, and the voltage must be maintained between 12V and 24V. If the voltage exceeds the permissible limit, the meter may be damaged.

- 2. The frequency of meter reading should not be too high to avoid affecting the measurement accuracy of the meter and the lifespan of the battery.

- Transmission Method

- Information is transmitted asynchronously in bytes.

- The communication messages exchanged between the master and slave devices follow a 10-bit format, which includes:

- - 1 start bit, 8 data bits (the least significant bit is sent first), no parity bit, and 1 stop bit.  The default baud rate is 9600 bps.

- Data frame format

| Address | - XX | - 1byte |
| --- | --- | --- |
| Function Code | - 0x03 | - 1byte |
| Starting Register High Address | - 0x10 | - n bytes |
| Starting Register Low Address | - 0x10 | - n bytes |
| Number of Registers High | - 0x00 | - n bytes |
| Number of Registers Low | - 0x0C | - n bytes |
| CRC Check Low Byte | - XX | - 2 bytes |
| CRC Check High Byte | - XX |  |

Address:

- The meter address can be configured within the range of 1 to 247 (Note: Address 104 is reserved and cannot be used). In hexadecimal representation, this range is 0x01 to 0xF7.

- These bits represent the user-assigned address of the terminal device that will receive data from the connected host. Each terminal device must have a unique address, and only the addressed terminal will respond to a query containing its address. When the terminal sends a response, the slave address data in the response informs the host which terminal it is communicating with.

| Function Code | Definition | Control Function |
| --- | --- | --- |
| 03H | Read Data Registers | Retrieve the current binary value of one or more registers |

- Function Code:
The function code informs the addressed terminal (slave) about the specific operation to be performed. The table below lists the function codes used in this series of meters, along with their meanings and functions.

- Data Field:
The data field contains the information required for the terminal to execute the specified function or the data collected by the terminal in response to a query. The content of this field may include values, reference addresses, or setting parameters. For example, when the function code instructs the terminal to read registers, the data field specifies the starting register address and the number of registers to read. The embedded address and data may vary depending on the type of slave device and its specific content.

- CRC Checksum:
The CRC (Cyclic Redundancy Check) checksum is calculated for the data frame, and the resulting two-byte checksum is appended to the end of the frame. The low byte of the CRC is placed first, followed by the high byte. The CRC calculation covers all data from the "Address" field to the "Low Byte of Register Quantity." The CRC field occupies 2 bytes and contains a 16-bit binary value, with the low 8 bits transmitted first and the high 8 bits transmitted last. The CRC value is calculated by the transmitting device and appended to the data frame. The receiving device recalculates the CRC during data reception and compares it with the received CRC value. If the two values do not match, an error is indicated. The CRC calculation range includes all data from the address field to the data preceding the CRC field.

- In summary, for a Modbus data frame sent from the master, only two parts are variable: the address field and the CRC checksum.

- CRC Generation Process:

- Initialize a 16-bit register with 0xFFFF (all bits set to 1), referred to as the CRC register.

- Perform an XOR operation between the 8-bit data of the first byte in the frame and the low byte of the CRC register, then store the result back into the CRC register.

- Shift the CRC register one bit to the right, filling the highest bit with 0 and checking the shifted-out lowest bit.

- If the lowest bit is 0, repeat step 3 (perform the next shift). If the lowest bit is 1, perform an XOR operation between the CRC register and a fixed preset value (0xA001).

- Repeat steps 3 and 4 until 8 shifts are completed. This completes the processing of one byte.

- Repeat steps 2 to 5 to process the next byte until all bytes in the frame are processed.

- The final value in the CRC register is the CRC checksum.

- Additionally, there is a method for calculating CRC using a predefined lookup table, which is faster but requires more storage space. This method is not discussed here; please refer to relevant documentation for details.

- (3) Communication Request Format
Function Code 03H: Read Registers
This function code allows the user to retrieve data collected and recorded by the device, as well as system parameters. The host can request any amount of data in a single request, but the requested data must not exceed the defined address range.

- The following example demonstrates reading basic data from a slave device with address 01 (each address in the data frame occupies 2 bytes). The collected data is the forward cumulative flow (occupying 2 registers, totaling 4 bytes), with register addresses 4118 and 4119. The corresponding hexadecimal value for these addresses is 0x1016.

- The data frame for the issued command is as follows:

01 03 10 16 00 02 21 0F

| Host sending |  | Send a message |
| --- | --- | --- |
| Address code |  | 01H |
| Function code |  | 03H |
| Start address | High byte | 10H |
|  | Low byte | 16H |
| Number of registers | High byte | 00H |
|  | Low byte | 02H |
| CRC check code | Low byte | 21H |
|  | High byte | 0FH |

| Slave return |  | Return information |
| --- | --- | --- |
| Address code |  | 01H |
| Function code |  | 03H |
| Number of bytes |  | 04H |
| Register data | High byte | 00H |
|  | Low byte | 12H |
| Register data | High byte | D6H |
|  | Low byte | 87H |
| CRC Check code | Low byte | 44H |
|  | High byte | 34H |

- Explanation of Data Representation and Format:

- In the table, the measured reading is represented by 4 bytes and is expressed in cubic meters (m³). The data follows the "high byte first, low byte later" convention. For example, if the read value is 0012D687H (1234567 in decimal), the measured value is calculated as:
1234567 × 0.01 = 12345.67 m³.

- The meter collects data based on the data frame sent by the master station and constructs a Modbus data frame to return to the master. The meter fills the "data field" in the table, ensuring that each data item follows the high-byte-first, low-byte-later rule. Below are examples to illustrate this:

- Example 1:

- Data ltem (Decimal):12345

- Hexadecimal Representation: 0x3039Byte Representation (2 bytes):

- High byte: 0x30  Low byte: 0x39

- Byte Order in Data Frame: 0x30 0x39

- Example 2:

- Data ltem (Decimal): 1234567

- Hexadecimal Representation: 0x12D687

- Byte Representation (4 bytes):

- o High byte of the high word: 0x00

- Low byte of the high word: 0x12

- High byte of the low word: 0xD6。

- Low byte of the low word: 0x87D

- Byte Order in Data Frame: 0x00 0x12 0xD6 0x87

- (4)MODBUS register allocation list

- The instrument has 15 register addresses within the range of 4112 to 4126 (represented in hexadecimal as 0x1010 to 0x101B). Each register has a data length of two bytes.If tested with modscan software, the register address bit needs to be read starting from 4113.

| Register address Hex | Register address Dec | Register count | Variable name | Unit | Number of bytes |
| --- | --- | --- | --- | --- | --- |
| 1010H | 4112 | 1 | Battery voltage | 0.01V | 2 bytes |
| 1011H | 4113 | 1 | Water supply temperature | 0.01℃ | 2 bytes |
| 1012H 1013H | 4114-4115 | 2 | Reverse cumulative flow | L | 4 bytes |
| 1014H 1015H | 4116-4117 | 2 | Reverse instantaneous flow | L | 4 bytes |
| 1016H 1017H | 4118-4119 | 2 | Forward cumulative flow | L | 4 bytes |
| 1018H 1019H | 4120-4121 | 2 | Forward instantaneous flow | L | 4 bytes |
| 1020H | 4122 | 1 | Alarm status | High byte ST1 | 2 bytes |
| 1021H | 4123 | 1 | Alarm status | Low byte ST1 | 2 bytes |

- (5) Table of units

Cumulative flow unit:                                                      Instantaneous flow unit:

| 0C 10 | 1mL |
| --- | --- |
| 0C 11 | 10mL |
| 0C 12 | 100mL |
| 0C 13 | 1L |

| 0B 38 | 1mL/h |
| --- | --- |
| 0B 39 | 10mL/h |
| 0B 3A | 100mL/h |
| 0B 3B | 1L/h |

- Description of the data item filled in the data area：

| Data item | Unit | Caliber | Decimal point | Number of bytes | Group the magnification of the data frame |
| --- | --- | --- | --- | --- | --- |
| Water temperature | ℃ | All | 0.01 | 2 | 100 |
| Cumulative flow | m³ | DN50-400 | 0.001 | 4 | 10 |
| Instantaneous flow | m³/h | DN50-150 | 0.01 | 4 | 100 |
|  |  | DN200-400 | 0.1 | 4 | 10 |

- (6)Data frame example

When the meter address (S/N) is 1:

Host sends data frame:   01 03 10 10 00 0C 40 CA

Meter returns data frame:

01 03 18 01 68 12 02 00 BC 61 4E 00 CB 21 34 00 45 9B 7D 03 62 88 14 00 20 03 00 67 B5

| Meter returns data frame | Instructions（Hexadecimal to decimal） |
| --- | --- |
| 01 | Mailing address |
| 03 | Function code |
| 18 | Byte length (register) |
| 01 68 | Battery voltage (3.57V) |
| 12 02 | Water temperature (46.1℃) |
| 00 BC 61 4E | Reverse cumulative flow（4561.789m³） |
| 00 CB 21 34 | Reverse instantaneous flow（14.356m³/h） |
| 00 45 9B 7D | Forward cumulative flow (4561.789m³) |
| 00 62 88 14 | Forward instantaneous flow (14.356m³/h) |
| 00 20 | Alarm status ST1（High byte reserved, 00 not parsed） |
| 03 00 | Alarm status ST2（Low byte reserved, 00 not parsed） |
| 67 B5 | CRC check |

- Status word parsing

- ST1

| Bit 0 | 0 normal 1 Flow overload | Bit 4 | Reserve |
| --- | --- | --- | --- |
| Bit 1 | Reserve | Bit 5 | 0 normal 1 Lack of water |
| Bit 2 | 0 normal 1 undervoltage | Bit 6 | Reserve |
| Bit 3 | Reserve | Bit 7 | Reserve |

- ST2

| Bit 0 | 0 normal 1 Sensor ① lack of water | Bit 4 | Reserve |
| --- | --- | --- | --- |
| Bit 1 | 0 normal 1 Sensor ② lack of water | Bit 5 | Reserve |
| Bit 2 | Reserve | Bit 6 | Reserve |
| Bit 3 | Reserve | Bit 7 | Reserve |

Parsing example:

Register 4122 has a value of 0020  ST1=20H

20H to BIN= 0010 0000 (From right to left, Bit0,Bit1,···Bit7)

Parsing by status word:

Bit5=1   Lack of water

Register 4123 has a value of 0003  ST2=03H

03H to BIN= 0011 (From right to left, Bit0,Bit1,···Bit7)

Parsing by status word:

Bit0=1   Sensor ① lack of water    Bit1=1   Sensor ② lack of water

- Note: If ModScan is used for communication testing, the starting address of the registers should be observed beginning from 4112.

Wiring Method：

The communication address of the instrument is derived by taking the last two digits of the S/N (Serial Number). The communication address is displayed in hexadecimal format. If necessary,please convert it to decimal format, referring to the data sheet below.

Note: In the S/N, 68 corresponds to 104, and 00 corresponds to 0. These two addresses are unavailable for use.

Communication Address Mapping Table

| HEX（S/N） | DEC | HEX（S/N） | DEC | HEX（S/N） | DEC |
| --- | --- | --- | --- | --- | --- |
| 01 | 1 | 34 | 52 | 67 | 103 |
| 02 | 2 | 35 | 53 | 68 | 104 |
| 03 | 3 | 36 | 54 | 69 | 105 |
| 04 | 4 | 37 | 55 | 70 | 112 |
| 05 | 5 | 38 | 56 | 71 | 113 |
| 06 | 6 | 39 | 57 | 72 | 114 |
| 07 | 7 | 40 | 64 | 73 | 115 |
| 08 | 8 | 41 | 65 | 74 | 116 |
| 09 | 9 | 42 | 66 | 75 | 117 |
| 10 | 16 | 43 | 67 | 76 | 118 |
| 11 | 17 | 44 | 68 | 77 | 119 |
| 12 | 18 | 45 | 69 | 78 | 120 |
| 13 | 19 | 46 | 70 | 79 | 121 |
| 14 | 20 | 47 | 71 | 80 | 128 |
| 15 | 21 | 48 | 72 | 81 | 129 |
| 16 | 22 | 49 | 73 | 82 | 130 |
| 17 | 23 | 50 | 80 | 83 | 131 |
| 18 | 24 | 51 | 81 | 84 | 132 |
| 19 | 25 | 52 | 82 | 85 | 133 |
| 20 | 32 | 53 | 83 | 86 | 134 |
| 21 | 33 | 54 | 84 | 87 | 135 |
| 22 | 34 | 55 | 85 | 88 | 136 |
| 23 | 35 | 56 | 86 | 89 | 137 |
| 24 | 36 | 57 | 87 | 90 | 144 |
| 25 | 37 | 58 | 88 | 91 | 145 |
| 26 | 38 | 59 | 89 | 92 | 146 |
| 27 | 39 | 60 | 96 | 93 | 147 |
| 28 | 40 | 61 | 97 | 94 | 148 |
| 29 | 41 | 62 | 98 | 95 | 149 |
| 30 | 48 | 63 | 99 | 96 | 150 |
| 31 | 49 | 64 | 100 | 97 | 151 |
| 32 | 50 | 65 | 101 | 98 | 152 |
| 33 | 51 | 66 | 102 | 99 | 153 |